August 23, 2007

Mr. Jeff Bragdon, P.E.

McKinney & Company

100 South Railroad Avenue

Ashland, Virginia     23005

RE:	Eastport VII

5950 Eastport Boulevard

File No. 2974 – P.O.D. No. 62-97

Dear Mr. Bragdon:

Enclosed are marked-up prints of the water and sewer plans that are part of the plan of development submitted to the Planning Department on August 21, 2007.

DPU recommends approval of these plans by The Planning Commission.

Please address the following comments before submitting the construction plans for signature.

Cover Sheet:

1.	Include “POD and Utility Plan” in the title of this project.

Sheet C-002:

2.	If any public utilities are on the site they should be indicated on this sheet.  If they will remain add the following note, “Minimum cover is to be maintained over at all times during demolition and construction.”

3.	If there are any utilities and they will be abandoned, provide the following note on the plan, “All utilities that need to be abandoned will be done so in accordance with DPU Standards 1.1.04C and 9.3.10.”

Sheet C-101:

4.	Provide a reference for the CSB/CWB sheets for this project.  See Sheet 301 as well.

5.	Provide CSB station, rim and invert information for all existing manholes shown on the plan.  See Sheet 301 as well.

6.	Provide the size and material type of the existing water and sewer mains.  See Sheet 301 as well.

7.	The proposed sewer is not required to be shown on this plan sheet.

Sheet C-301:

8.	DPU does not allow cross county water main.  Remove the cross country water main from the plan and extend the water main for the east side of the building from Eastport Drive.  This will also reduce the amount of water main required to serve this site.

9.	Henrico DPU does not allow the installation of 10” water main.  All mains shown as 10” must be installed as 12” unless hydraulic calculations prove that an 8” main is adequate.

10.	All 12” water main installed must be ductile iron per DPU Standards.

11.	The complete size of the tee must be called out.  If a tee is 12” x 8”, this must be indicated on the plan.

12.	All backflow preventer callouts must include the size of the backflow preventer, as well as the sheet location of the detail.

13.	The water main installed on site should be called out as a water main and not a fire water line.  The fire water line callout is reserved for the private line with the Siamese connection.

14.	The fire hydrants installed at the end of the 8” main should be done so with an 8” x 6” tee and plug, not a reducer and bend.

15.	The fire hydrant installed off of the 8” main near the western entrance should be done so with an 8” x 6” tee.

16.	All fire hydrant valves should be installed adjacent to the main and not the hydrant in accordance with DPU Standard Detail D-200.

17.	Review the water main being installed at the western project entrance.  The water main and valves should be installed so that they are not within the gutter pan.

18.	Be advised that the standard detector check is not traffic rated.  In its proposed location, it must be protected from traffic loading.  Revise the location or provide traffic protection for the detector check.

19.	Will having the Siamese connection in the general vicinity of the electric garden pose a safety hazard?

20.	Review the fire hydrant shown on the east side of the building.  The fire hydrant should be installed inside of the area of the bollards.

21.	Provide the core drill note on this plan sheet.  It may remain on Sheet 306 as well.

22.	Indicate that the run of 8” sewer is private.

23.	Provide material type, length and slope of the proposed sewer main.

24.	Provide a note indicating that the proposed manhole will be acid resistive and the existing public manhole that the onsite sewer system connects to will also be treated with acid-resistive coating.

25.	Based on a review of the force main profile, consider revising the location of the proposed manhole and force main connection.  This will allow the force main to be more easily maintained in the future.  See the attached drawing and/or marked up plan for clarification.

26.	Indicate the capacity of the pump station for this project.

Sheet C-302:

27.	Review the title of this sheet, there are no utility profiles indicated on this sheet.  The one profile dealing with utilities is labeled as a storm profile.

General:

28.	Agreements have not been executed for this project.  This project cannot be approved until Agreements have been executed by the Owner and the County.

29.	Plans were submitted directly to DPU for review.  Since this is a POD, all subsequent review submittals, unless otherwise directed, should be submitted to the Planning Department for routing.

If you have any questions concerning the above noted comments or the plans, please contact me at 501-4500.

Sincerely,

Alvin E. Christian, Jr., P.E.

Senior Engineer, Private Development

Enclosure

cc:	Mr. Dana Dame, Liberty Property Trust

bc:	Jim Strauss/Planning via e-mail

R. Claytor

A. Seal

Reading File

AEC/cca