OIL/WATER SEPARATOR COMMENTS

Project Name:  BJs Regency Square	POD #:

Date:  9/4/07

IF THE WASTEWATER WILL BE DIVERTED TO THE STORM SEWER SYSTEM:

(Checked items must be addressed)

1.  The Oil/Water Separator (OWS) must be designed according to the American

Petroleum Institute (API) standards.

A.  If the OWS will be designed by the engineer, the design calculations and

details must be submitted for review.

B.  If a pre-manufactured OWS will be used, the following information must be

submitted for review:

a.  The design calculations for sizing the OWS

Q = A x I

Where :	Q  is the design flow to the OWS

A is the area draining to the OWS

I is the amount of rainfall = 1.6 in/hr under the canopy

= 2.8 in/hr outside of canopy

b.	A statement from the manufacturer indicating that the OWS is                             designed per the API standards.

c.  A detail drawing of the OWS must be shown on the plans.

2.	A trench drain system must be installed to divert the wastewater to the OWS.

3.	The trench drain must fully encompass the area that produces wastewater.

4.	The area that produces wastewater must be covered.  The canopy must be labeled and the trench drain should be inside the drip edge of the canopy.

5.	The area that produces wastewater must be graded so the runoff from the surrounding area will not enter the trench drain.  Spot grades around the fueling pad must be shown on the plans.

Comments: