October 9, 2007

Mr. Mathew L. Schliske, P.E.

Kimley-Horn & Associates, Inc.

501 Independence Parkway

Suite 300

Chesapeake, Virginia     23320

RE:	Hyatt Place at

The Shops at White Oak Village

South Laburnum Avenue

File No. 4825 – P.O.D. No. 072-07

Dear Mr. Schliske:

The following comments regarding the water and sewer plans that are part of the plan of development submitted to the Planning Department on September 14, 2007.

DPU recommends approval of these plans by The Planning Commission.

Please address the following comments before submitting the construction plans for signature.

General Comments:

1.	The proposed water and sewer utilities are not consistent with previously approved utility plans for the Shops at White Oak Village as prepared by Vanasse Hangen Brustlin for Forest City Commercial Group.  A revision to this previously approved plan must be coordinated with this plan and approved prior to approval of construction plans for this facility.

2.	Revise the DPU Standard Details as follows:

  - Replace D-240 for the 6” Detector Check on Sheet CU501 with D-241 for an 8” Detector Check since an 8” Detector Check is called out on the utility plans.

  - Replace Detail A-13 on Sheet CU502 with A-15 since a high hazard backflow prevention device will be needed.

3.	Provide Approximate Water and Sewer Quantities on the plans.

4.	Provide the attached DPU Material Notes on the plans.

5.	Revise the DPU Review Checklist as follows:

a.	Provide answers to Items 3.a, 4.b, 5, 10, 13, 16, and 17.

b.	It appears that Item 3.c, the Design Fire Flow should be 2000 GPM

  - Use 130 gpd/room as a basis for average water and sewer flows.  Equivalent Residential unit is 300 gpd/unit.

  - In Item 3, the required waterline size is 8”.

6.	An Information Sheet for Preparation of Agreements for Water and/or Sewer Service is required but has not yet been submitted.  The Information Sheet allows the Department of Public Utilities to prepare the Water and Sewer Agreements which must then be executed by the Owner and the County prior to approval of building permits or prior to the utility pre-construction meeting and authorization to proceed with utility construction.  It is recommended that the Information Sheet be submitted as soon as possible to avoid delays in either of these steps.  Preparation of the Agreements may take up to 15 days after receipt of the Information Sheet and execution by the County after execution by the Owner may take up to 10 days.  Conflicts between the completed Information Sheet and the plans may generate additional review comments.

7.	The DPU Monitoring and Compliance Division is currently reviewing the NOI form information.  Any comments requiring further action will be forwarded to you upon receipt by our office.

Sheet CU101:

8.	Add the following Note to the cover sheet: The water and sewer systems for this project will not be accepted, nor will connections be allowed to County water and sewer systems until the water and downstream sanitary sewer proposed on the utility plan for The Shops at White Oak Village, DPU Drawing File No. 2007-071 is accepted by the County for operation.

9.	Cluster both of the 8” gate valves with adjacent tees and branch valves.

10.	Reference DPU CSB/CWB Pages 78SE and 117SW in the lower right hand corner of this sheet.

11.	Provide four (4) minimum GIS (Northing/Easting) reference points on the utility plan sheet.

12.	Show the location of the closest valves for each of the two existing waterline stubs or provide a call-out note describing the location of these valves.

13.	Remove the bend from the lead for the fire hydrant located near the eastern entrance to the development.  Locate the hydrant and lead within pavement and cluster with the nearby 8” valve.  Please note that a hydrant has already been installed at the right side of the northeastern entrance in a location acceptable to DPU in lieu of this proposed hydrant.

14.	DPU is in agreement with the proposed location of the fire hydrant located adjacent to the northwest corner of the proposed building.  However, a request for an exception to DPU Standards Section 4.2.05 will be needed since the hydrant is located less than 50’ from the proposed building.

15.	Revise the location of the proposed fire department connection (FDC), placing it in the traffic island just south of the meter and detector check locations, adjacent to the proposed fire hydrant.  The fire hydrant located in this island should be designated as the dedicated hydrant.  This will allow for full circulation around the site in case of a fire while the sprinkler system is being operated.

16.	Call-out and show all backflow prevention devices (domestic, fire, irrigation) on the plans.  Reference and include the appropriate DPU Standard Detail for each.

17.	DPU suggests the use of dual 2” water meters (per DPU Standard Detail D-223) instead of a 3” meter as proposed.  The 3” meter would have to be special ordered and the connection fee for dual 2” meters is slightly cheaper than that of a 3” meter.

18.	Dimension the distance between the monitoring well and the proposed waterline.  There should be a minimum of 5’ separation between the two.

19.	Provide benchmarks consistent with DPU Spec. 1.2.02.I.(6).

20.	The run of 8” sewer between MH1 and MH 2 should be private.  MH 2 should be designated as a “monitoring manhole.”  Reference DPU Standard Detail D-114 at the monitoring manhole and include the detail on the plan.

21.	Provide an internal angle at MH2.

22.	It appears that MH2 will need to be constructed with the plans for The Shops at White Oak Village and, therefore, should be labeled as an existing manhole.

23.	Profile the proposed run of sewer from MH1 to MH2.

24.	Provide a detail for the grease interceptor and specify the volume for this unit.

25.	Please describe the food preparation facilities.  Will there be a restaurant within this hotel?

26.	Show field verified location of the 60” sewerage force main.

CU102:

27.	Provide the irrigation demand on the meter sizing form.

Sheet CI101:

28.	Revise the landscaping plan as follows:

a.	Tree plantings shall be located outside of all easements or at least 10 feet away from utilities within right of ways.

b.	Other non-tree type landscaping shall not conflict with or obscure visibility of utilities at or above grade (i.e., hydrants, meter vaults, detector check vaults, valve boxes, etc.).

c.	For any non-tree type landscaping within easement or within 10 feet of utilities in a right of way, provide the following note on the plan: “The Owner is responsible for replacement of any planting (i.e. shrubs, etc.) damaged or removed by DPU, or it’s Agent, as required for maintenance of County owned water and/or sewer facilities.”

d.	There shall be no light pole structures within or overhead of any county easements, or within 10 feet of utilities within the right of way.

29.	As previously discussed and agreed to, please provide a layout of the irrigation system versus the 60” force main and easement for DPU evaluation and concurrence.  All irrigation system components must be located at least 10’ away from the force main.  Where not possible, DPU will require a letter from the owner indemnifying DPU from replacing or repairing this system from any damage should it occur during activities related to operation and maintenance or repair of the force main and associated appurtenances.

If you have any questions concerning the above noted comments or the plans, please contact me at 501-4501 or Jarad Morton at 501-4511.

Sincerely,

John L. Clark, P.E.

Utilities Engineer II

cc:	Mr. Prakash Rajamani, LTD Management Company, LLC

Mr. Mitch Mitchell, Vanasse, Hangen, Brustlin, Inc.

Mr. Brendan Fisher, Forest City Commercial Development

bc:	Jim Strauss/Planning via e-mail

R. Claytor

A. Seal

J. Morton

Reading File

JLM/cca