April 24, 2008

Joseph Vilseck III, P.E.

Timmons Group

1001 Boulders Parkway, Suite 300

Richmond, VA 23225

RE: 	Harbor Village Apartments Clubhouse

2337 Harpoon Court

File No. 4940; POD No. 028-78

Dear Mr. Vilseck:

We have reviewed the construction plans submitted to the Planning Department on April 17, 2008.

Please address the following comments and resubmit revised construction plans for review.  Water and Sewer Agreements that must be executed by the Owner and the County have not been executed.

Sheet C2.0:

- As previously commented, show the location of all existing utilities on the plan in accordance with the CWB sheets.  See Sheet C4.1 as well.

Sheet C3.0:

- As previously commented, provide the direction of flow arrows on all existing sewer mains shown on the plan.  See Sheets C4.1 as well.

- As previously commented, provide the CSB station, rim, and invert information for all existing manholes shown on the plan.  See Sheet C4.1 as well.  Be sure to label the CSB information as “CSB” and field surveyed information as “FIELD.”

- The top and invert information shown for the existing manholes in Clipper Court appears to be incorrect.  Review and revise in accordance with the CSB sheet.

Sheet C4.1:

- As previously commented, indicate the material type of the existing water mains on the plan.  If the material type cannot be determined, indicate the material type as “unknown” on the utility plan.

- As previously commented, indicate the size of the existing meter serving the existing building to be demolished on the utility plan. Also, indicate the meter number for the existing meter as well.

- Install the valve on the fire hydrant lead near the tee in accordance with the fire hydrant detail (D-200).   Review and revise the proposed fire hydrant.

- A tee should not be installed in a water main that is already in service. Installation of a tee will require a water main shutdown.  Use a 6” x 6” TS&V to connect the fire hydrant to the existing 6” water main in Harpoon Court

- Review the existing 6” waterline in Harpoon Court located south of Apartment Building (#2342-#2353).  According to the CWB Sheets and Geographical Information System (GIS), there is no existing 6” water line located south of Apartment Building (#2342-#2353).  Survey the site to verify if a 6” water line was installed in that location.

- As previously commented, based on the available flow in the existing 6” water line in Harpoon Court, the required fire flow for this project is not available.  The following options are provided to addressed to above comment:

  - Install a sprinkler system or change the type of construction (class) on the Fire Flow Estimate Form to reduce the Required Fire Flow for this project.

  - Upgrade the existing 6” water line in Harpoon Court to an 8” water main to obtain the Required Fire Flow.

  - Connect to the existing 8” water main in Clipper Court using an 8” x 8” TS&V, extend an 8’ water main in Harpoon Court and connect the proposed fire hydrant north of Apartment Building (#2362-#2369) to the 8” water main in Harpoon Court.

- According to the billing system, the whole apartment complex is not served by a master meter.  There are multiple meters onsite that serves more than one building.  Show the location of the meter that serves the existing building to be demolished, per comment #6.  Consider surveying the site to determine the location of the water meter. Be sure to revise Note-2 in the note box located in the bottom right corner of plan sheet as well.

Sheet C4.2:

- As previously commented, the exposure and communication values on the Fire Flow Estimate Form appears to be incorrect.  Be sure to include the exposure on the east side of the proposed building as well.  Review and revise as necessary.

General:

- Provide DPU with a hard copy of the completed NOI form required per Monitoring and Compliance Department.

- The Meter Sizing Form for the proposed project was not included in the plan submittal or provided on the plan.  All of the comments regarding the Meter Sizing Form that were provided on the comment letter dated March 10, 2008 need to be addressed. Also, be sure to provide the Meter Sizing Form on the plan as well.

- The Review Checklist for the proposed project was not included in the plan submittal.  All of the comments regarding the Review Checklist that were provided on the comment letter dated March 10, 2008 need to be addressed. Provide DPU with a hard copy of the revised Review Checklist.

- As previously commented, if an additional fire hydrant will be installed, provide a completed green card application for preparation of Agreement.

If you have any questions concerning the above comments or the plans, please contact me at 501-4508 or Bentley Chan at 501-7543.

Sincerely,

Alice Jackson

Utilities Engineer