The Engineering Division has completed its review of the above referenced project and has the following comments:

The following information was provided on the approved plan from 1998, but omitted from this revised set of plans.  Please include this information to the revised set of plans:

- O-ring joints on the storm sewer pipes.

- Routing calculations and details of the basin and control structure of the BMP.

- Details and calculations of the down stream channel / pipes to show they are adequate.

- Water Quality Calculations for the revised plan.  Show the BMP is adequate for the future expansion.

- Cut and fill balance for the 100-year flood plain on site.

The following information needs correcting on the revised set of plans:

- The Sanitary Sewer profile on Page C-302 has the structures labeled as “storm sewer”.

- The profile of Storm Sewer Segment (6-1) on Page C303 has the last structure labeled as #7 instead of #1.

- Use the 10-year elevation in the BMP as the starting elevation for the 10-year Hydraulic Grade line calculations.

- Check the Hydraulic Grade Line Calculations, especially for Hfinal and Outlet Surface Elevation.

Reviewed by:	Steve Bandura

Date Reviewed:	27aug07

Phone Number:	804-501-4616		Revised 1/2/07