Henrico County Division of Fire

Office OF THE FIRE MARSHAL

# STAFF / DEVELOPER COMMENTS

DATE Due:	10/2/09

PROJECt:mini price warehouse

pLANNEr: greg garrison

Pod –031-09

TIDEMARK#POD2009-00340

- Provide ISO calculations for all structures planned on 1981 rating schedule.

- Provide hydrants to satisfy needed fire flow as established by the ISO calculations.  The following

GPM credits, as per ISO Standards will apply.  Hydrant within 300 ft. of structure = 1000 GPM; 301 ft. to 600 ft. = 670 GPM; over 600 ft. = 250 GPM.

- Hydrants must be within a 350-ft. hose lay of the building circumference, a minimum  of 50 ft. from

the structure wall and accessible to fire department apparatus.  Measure hose as laid from apparatus.

- Hydrants must be between 1½  ft. and 7 ft. from the curb line and have 4 inch opening facing the street,

unless otherwise instructed.

- All structures must be accessible on all four sides to emergency equipment.  A minimum of 20 ft.

roadway width is required. A 150’ hose from the apparatus must reach all points of the exterior of a building.

- If railway delivery is part of operations, fire department access by a 20 ft. roadway must be provided to

the area of the property.

- Relocate hydrants as shown on plans.

- Provide dedicated hydrants to serve as supply for fire department connections.  Fire department

connection should be remote from the building and within 50 feet of the dedicated hydrant.

- Fire lanes may be required, minimum 20 foot in width, with turning radius of 48 foot to accommodate

fire department apparatus.

- No fire hose lay allowed across four (48 foot or more) roadway travel lanes.

STANDARD COMMENTS:

- Designation and marking of fire lanes to be determined prior to C.O. You may provide a layout plan sheet for fire lane designation. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of  “lock boxes” in all commercial construction.

- The installation of speed bumps may increase the response time of emergency vehicles, resulting in the decreased protection of life and property.

- If gates are part of this project, a separate plan showing details of all required features must be submitted for approval. Failure to obtain approval prior to construction of gates may result in the gates being locked in an open position until approval can be obtained by order of the Chief Fire Marshal.

- These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the Va Statewide Fire Prevention Code, which identifies the International Fire Code 2006 edition as a technical reference.

- If the type of construction and the layout of the building or buildings prevent adequate performance of the radio system utilized by emergency services, the owners will be required to install the necessary devices to obtain radio coverage inside the buildings.

ADDITIONAL COMMENTS:

  - Please show the location of DFH and FDC.

  - Hose lay shall not be more than 350 feet to the most remote part of the building.(exterior)

  - FH shall be 50 feet away from the building, out of the collapse zone.

  - Fire lane shall be provided all around the building, min . 20 feet wide

  - Where parking is provided and the apparatus is using the space between the parked car , the clear space shall be 30 feet.

For additional information or clarifications, call 501 – 5793.

9/24/2009			        		     	 Russell  Rastegar

DATE  						REVIEWER, DIVISION OF FIRE

Fire protection engineer