The Engineering Division has completed its review of the above referenced project and has the following comments:

- Adjust / record a new drainage easement along Pipe Segment (44-46) and though the basin.

- There are two Spot Elevations in the parking area labeled as “T/C elevations”.

- The Riser Pipe needs to be made of RCP.  Adjust the base dimensions accordingly.

- Provide the dimensions on the expanded basin.

- Label the Water Quality Elevation of the basin in the plan view.

- Provide the hydraulic calculations, (capacity, HGL, etc.), of the existing pipe system the basin is discharging into.

- How was the discharge rate from the basin determined?

- Who owns the pipe system the basin is discharging into?  Show any existing offsite Public or Private drainage easements or provide evidence you can discharge into the pipe system if private.

- Profile the proposed cover over existing outfall pipe in the basin.  Should the riser be relocated more into the side of the basin?

- Since the existing discharge pipe in the basin is being graded over and will have standing water above it provide anti-seep collars on the pipe.

- Why was a Site Area of 10-acres used in the on “Worksheet 2.1 – Program Implementation”, and 15.18-acres used in the Water Quality Calculations?

- Include the “Outfall Structure Input Data” on the plans on Page 7 of 11.

- Provide a copy of the routing calculations for Public Works’ file.

- Label the storm intensities, (2-yr, 10-yr, etc.) of the “Summary of Routing Computations” on Page 7 of11.

- Structure #45 needs to be a DI-4 series inlet.

Reviewed by:	Steve Bandura

Date Reviewed:	16sept10

Phone Number:	804-501-4616		Revised 8/11/08