Is a Pre-Construction Meeting required?						Yes  No

ENVIRONMENTAL SITE ASSESSMENT:

- The completed Environmental Site Assessment (ESA) must be included with the plans.  (A complete plan review can not be accomplished until this information has been provided.  Once this information has been received, additional comments may follow.)

- ESA number(s)   7,8   was (were) answered incorrectly.

- The current version of the two standard Erosion and Sediment Control sheets entitled “Standard Notes” and Standard Details/Calcs.”, revised 4/15/09, must be included the plans.

- The owner must sign the Acknowledgments on the Minimum Design Standards for ESC sheet.

ADDITIONAL COMMENTS:

  - ESA items 7 and 8 need to be "yes"

CHESAPEAKE BAY PRESERVATION AREAS / STREAM PROTECTION AREAS:

- The following land features are present on the site and must be accurately shown on the plans:

Resource Protection Area (RPA)

Resource Management Area (RMA)

Stream Protection Area (SPA) (non-RPA and 100 acres or more of drainage)

- A RPA appears to exist on the site associated with a perennial stream that has not been previously identified as such.  In accordance with County Code, RPA rules apply to the stream.  Under this circumstance, appropriate evidence will need to be provided to claim that the stream is not perennial and that RPA rules do not apply.

- The SPA buffer must be forested/reforested if IPOST ≥ 16%.

- The plan must include reforestation details consistent with Minimum Standard 9.10 of the Henrico County Environmental Program Manual.

- The Resource Protection Area (RPA) limits are shown incorrectly.

- The Resource Management Area (RMA) limits are shown incorrectly.  (If the entire site is considered RMA, question #10 on the ESA must be answered as “yes”.)

- The Stream Protection Area (SPA) limits are shown incorrectly.

- There must be a setback equal to or greater than the minimum rear yard setback between the RPA/SPA limits and the rear of the buildable area.

- There must be a separation between the side yard buildable area and the RPA/SPA limits, including RPAs/SPAs in common areas, of at least 25 feet.

- Lots that contain a RPA must be identified with appropriate asterisks ( * ) and notes as stated on page 6-1 of the Henrico County Environmental Program Manual.

- Lots that contain a SPA must be identified with appropriate asterisks ( *** ) and notes as stated on page 11-4 of the Henrico County Environmental Program Manual.

- A maintenance agreement for the SPA must be provided.  A copy of the required maintenance agreement is available from the Department of Public Works.  Information and forms for the SPA maintenance agreement can be found at:  http://www.co.henrico.va.us/departments/works/forms/  (near the bottom of the page under SPA (Stream Protection Area) Agreement.

ADDITIONAL COMMENTS:

  - Per Robin Wilder - the stream bordering the northern boundary of the property that outfalls from the culverts under Broad Street is RPA.  A100' buffer needs to be shown from the appropriate RPA feature (side of stream channel, edge of associated wetland).

  - Show the RPA buffer boundary on all relevant sheets - Site Plan, Grading Plan, ESC Plan, Utility Plan.

ENVIRONMENTAL PROTECTION AREA SIGNS:

- Environmental Protection Area signs are required on all lots containing RPA/SPA and/or wetlands.  Sign locations must be accurately shown on the plans in accordance with the Sign Spacing, Location, and Installation Guidelines.

- The sequence of construction must clarify that the Environmental Protection Area signs must be installed prior to the pre-construction meeting and must be maintained throughout construction.

ADDITIONAL COMMENTS:

WETLANDS:

- Jurisdictional wetlands and/or other waters of the U.S. (WOUS) appear to exist on this site (Henrico County representatives do not have the authority to declare a site void of jurisdictional WOUS, including wetlands).

- We were unable to check the wetlands/WOUS delineation because the wetlands/WOUS were not accurately flagged in the field.  Please contact the Henrico County Water Quality Research Analyst at 727-8325 once the wetlands have been accurately flagged.  Final plans must reflect all such boundaries.

- Orange safety fence or non-tearable yellow and black barricade tape is required for all WOUS/wetlands to remain and/or at the limits of the RPA/SPA buffer.  It must also be installed around the limits of disturbance for all encroachments/impacts within these areas.  Show the location of fence/barricade tape on the plans.  The fence/tape must be installed prior to the pre-construction meeting (clearly note this in the ESC narrative).

- This activity has been determined to require Federal (U.S. Army Corps of Engineers) and/or State (Department of Environmental Quality (DEQ)) authorization for impacts to WOUS, including wetlands.  Please submit all applicable permits and associated maps or a certification from a principal in the engineering firm (with a copy sent to the Corps) that the proposed impacts are authorized by law.  Additional comments may be generated once the permits have been submitted; therefore, we recommend that all applicable permits be submitted as soon as possible.

- All wetland areas and WOUS must be accurately shown on the plans.

- All wetlands to be impacted (including WOUS) must be clearly identified and quantified on the plans.

- We disagree with the wetland delineation as currently shown.  We feel that there are additional wetlands located      .  If you disagree with this assessment, please contact Robin Wilder at 727-8325.

- There must be a setback equal to or greater than the minimum rear yard setback between wetlands/WOUS to remain and the buildable area.  The separation between the side yard buildable area and areas of wetlands/WOUS, including wetlands/WOUS in common areas, must be at least 25 feet.

- All wetlands/WOUS in front and side yards must be indicated as wetland impacts.

- Lots that contain non-impacted wetlands/WOUS must be identified with appropriate asterisks ( ** ) and notes as stated on page 7-2 of the Henrico County Environmental Program Manual.

- A 25 feet wide buffer measured from the streambank is required on both sides of the channel.  The buffer must remain undisturbed, delineated on the construction plans, and clearly marked in the field.

- There must be a setback equal to the front, rear, or side yard setback between the 25 feet buffer limits and the buildable area.

- Unless temporary construction limits are shown on the plans, land disturbance within wetlands/WOUS, SPAs, and/or RPAs will be restricted to the permanent easement width.

ADDITIONAL COMMENTS:

  - The edge of the WOUS needs to be clearly indicated for the stream between the subdivision and the retail area, and Barricade Tape installed at the limits.

  - Will proposed stream crossings be constructed with this plan or with the POD for retail?  Will they be permitted as part of this plan or the POD?

EROSION AND SEDIMENT CONTROL (ESC):

- Submit an ESC plan in accordance with Chapter 10 of the County Code.  A complete plan review cannot be provided until this information has been submitted.  Once this information has been submitted, additional comments may follow.

- Provide two copies of the standard ESC Agreement and an ESC Bond.  All Bonds must be cash, letter of credit, or certificate of deposit.  Information and the forms for the E and S agreement can be found at: http://www.co.henrico.va.us/works/pdfs/revisederosionandsedimentcontrolagreement08.pdf

- Provide an itemized list, including quantities, of all ESC devices on the plans.  The list must include the total amount of land disturbance and the approximate volume of any stockpiles.

- The ESC bond amount is set at $to be determined  .

- The preliminary limits of disturbance necessary for installation of the initial ESC measures must be clearly indicated on the plans.  This area of disturbance must be the minimum necessary to allow installation of the initial ESC measures and should include all areas necessary for installing the initial ESC measures, including stockpiles, borrow areas, staging areas, etc.

- The ultimate limits of disturbance must be clearly indicated on the plans.

- Silt fence is required and must be shown on the plans.

- Silt fence is needed in additional areas, as noted in the Additional Comments section below.

- Temporary sediment trap(s) is (are) required and must be shown on the plans.

- Temporary sediment basin(s) is (are) required and must be shown on the plans.

- The sediment basin/trap design details information table on the ESA sheet must be completed.

- All sediment basins/traps must be designed so that the wet storage volume elevation does not back water into the permanent storm sewer.

- Baffles are required for all sediment basins/traps that do not meet the required 2:1 flow length to width ratio.

- Stockpiles and appropriate ESC measures must be shown on the plans or the narrative must state that no stockpiles will be located on the site.

- ESC blanket/matting (B/M) is required for all proposed slopes that are steeper than 3:1.

- All concentrated flow down fill slopes must be contained within an adequate temporary or permanent channel, flume, or slope drain structure.

- An ESC narrative/sequence of construction must be included on the plans and must appropriately sequence the installation and maintenance of ESC measures throughout construction.

- The ESC sequence of construction must state that a pre-construction meeting with the Environmental Inspector must occur prior to any land disturbance on the site.

- The ESC sequence of construction must state that if construction does not commence for 180 days following the pre-construction meeting or if the project is dormant for 180 days during the construction phase, a new pre-construction meeting is required before construction can re-start.

- The ESC sequence of construction must clearly indicate that land disturbance outside the preliminary limits of disturbance may not occur until the initial ESC measures installation has been approved by the Environmental Inspector.

- The ESC sequence of construction must clearly indicate that all diversions, sediment basins/traps, and stockpiles must be seeded and mulched immediately upon construction.

- The ESC sequence of construction must include a statement that no erosion and sediment control measures can be removed without approval of the Environmental Inspector for the project.

- The ESC plan/sequence of construction must clearly show how runoff will be diverted into sediment basin(s) or trap(s) during all phases of construction (storm sewer, diversions, channels, etc.).

- Lots adjacent to or containing a sediment basin or trap that will not be converted to a BMP must be identified on the cover sheet, the plan sheet, and with notes stating that building permits will not be issued for these lots until the basins or traps have been removed.

- ESC measures must be shown for all lots adjacent to or containing WOUS/wetlands, SPA, and/or RPA.  Add a note to the ESC plan sheet stating that these measures will be installed prior to dwelling construction.

- All land disturbance associated with utility construction, including appropriate ESC measures, must be clearly indicated on the plans.

- Provide a construction entrance at all access points to the site.

- A vehicle wash rack(s) is required at all locations where construction vehicles will leave the site.

- A water supply is required for the wash rack.  Clearly show how the water will be provided.

- The wash area for the wash rack must drain to a sediment basin/trap.

- Provide inlet protection for all inlets.

- Clearly label all areas of Temporary Seeding (TS) and Permanent Seeding (PS) on the plans.

- A variance request must be submitted in writing because Minimum Standard (MS)       is not being met      .

ADDITIONAL COMMENTS:

- Can you eliminate one of the construction entrances on Broad Street?   it is easier to control mud tracking if all of the traffic is leaving site at a single point.

- Construction entrances will need a wash rack that drains to a basin or trap.  You will have to show additional diversion or piping to drain wash rack to a basin or trap.

- Show silt fence along entire front of property next to Broad Street.

- Between the sediment basin and the stockpile, expand the corridor of the Preliminary limits to allow for better access for construction.  (Make the area that is only 25' across 50' across).

- Can you combine the two sediment traps into a single sediment basin.  It will be easier to pipe the riser to an outfall than to have sediment trap outlets that look to outfall over your proposed entrance road.

- Sediment basin outfalls need to show outlet protection.

- Although you are showing diversion dike to the sediment basins, there is still alot of area collecting water between the dike and the super silt fence protecting the WOUS.  With that in mind, show a couple of stone points of relief in the super silt fence to allow for some of the water that will collect behind the silt fence to escape.

- Show rock check dams every 150-200 feet along diversion dikes

- Install EC-2 blanket and matting where diversions enter sediment basins.

- Regarding Comment #54 - Phase 2 plan still needs to indicate sediment traps and basins, as all the storm drain will need to drain to a basin or trap until the site is stabilized and the basins and traps can be removed.  Temporary piping and/or omitting pipe and/or blocking inlets/structures may be requried to acheive this.  The Phase 2 narrative also needs to state that all storm drain needs to drain to a basin/trap until the drainage area it serves is stabilized and the basin/trap can be removed.

- Phase 2 plan - Show EC-2 B/M for swale along Broad Street.  Also show B/M for steep slope next to western entrance to Broad Street, and any other area where proposed slope is steeper than 3:1.l

- Phase 2 plan - Culvert Inlet Protection as protection for sediment-laden water is not needed for the two culverts you are installing, as the water in the stream should be clean.  However, you still have to show standard outlet protection for each culvert at the upsteam and downstream ends.

- Indicate temporary and permanent seeding for all landscaped areas.  All building pads should also indicate temporary and permanent seeding unless active construction is to commence on the pad once it is graded.

- Phase 2 plan - Is there a way to locate stockpile closer to Sediment Basin.  I am concerned that you may have a problem draining the stockpile to the basin as Phase 2 construction progresses.

- Phase 2 plan - E&S details are needed regarding stream diversion for culvert installation.

- Phase 2 plan - I notice that one culvert crossing is being fully constructed, but the other only shows the pipe being placed.  Wouldn't it make sense to construct the second crossing as well?

- ESC Narrative - Wetlands Barrier Tape, RPA buffer protection tape, and Tree Protection Tape needs to be installed prior to Preconstruction Meeting so it can be checked by the Environmental Inspector at Precon.

- ESC Narrative - Phase 1, note 5 - Include stockpiles in the note regarding items to be immediately seeded and mulched.

BEST MANAGEMENT PRACTICES (BMPs):

- The ESC narrative must include details on how the sediment basin will be converted into the BMP.

- The ESC narrative must include topsoil application for all BMP areas that will be stabilized with vegetation.

- The ESC narrative must appropriately sequence “rough grading” and “final conformance” BMP inspections.

- The ESC narrative must clarify that an as-built certification must be filed for all BMPs/detention facilities prior to the ESC bond being released.  The as-built certification forms can be found at:  http://www.co.henrico.va.us/works/eesd/bmpcertification.html

ADDITIONAL COMMENTS:

  - Plans and narrative should call out that up-flo filters should not be installed until the drainage area to the filters is permanently stabilized.

NPDES:

- An Oil/Water Separator (OWS) is required for this project.  The following comments will apply if the wastewater will be diverted to the storm sewer system:

The OWS must be designed according to the American Petroleum Institute (API) standards.

If the engineer will design the OWS, the design calculations and details must be submitted for review.

If a pre-manufactured OWS will be used, the following information must be submitted for review:

The design calculations for sizing the OWS

Q = A x I

Where:	Q = the design flow to the OWS

A = the area draining to the OWS

I = the amount of rainfall (1.6 in/hr under the canopy)

(2.8 in/hr outside of the canopy)

A statement from the manufacturer indicating the OWS is designed per the API standards.

A detail drawing of the OWS must be shown on the plans.

A trench drain system must be installed to divert the wastewater to the OWS.

The trench drain must fully encompass the area that produces wastewater.

The area that produces wastewater must be covered.  The canopy must be labeled and the trench drain must be located inside the drip edge of the canopy.

The area that produces wastewater must be graded so that the runoff from the surrounding area will not enter the trench drain.  Spot grades around the fueling pad must be shown on the plans.

- This “industrial activity” may be required to obtain a NPDES permit for stormwater discharge along with a pollution prevention plan.  Please consider this in the design and development of this facility.

- The dumpster pad must be located so that it does not drain directly to the storm sewer system.

- Trash racks are required on storm sewer inlets.  Rebar must be located to provide a two-inch maximum clear space and must be either galvanized or epoxy coated.  Trash racks must be noted in the list of drainage descriptions and details must be provided on the plans.

- The plans must include a note on the plan cover sheet stating how the storage of bulk waste fat/oil/grease (FOG) will be addressed – either by using bins/barrels for storage or by using an indoor grease extraction unit.

- If barrels/bins are used for FOG storage, the plans must clearly show the location of the barrels/bins.

- The barrels/bins must be stored “under roof” to eliminate rainfall intrusion.

- A floor drain is required where the barrels/bins are located.  The floor drain must discharge to the sanitary sewer.

- Provide a detailed grading plan for the FOG storage area showing that the area “under roof” will drain to the floor drain and that the area that is not “under roof” will drain away from the storage area.

ADDITIONAL COMMENTS:

  - Restaurants with deep fat fryers will need to manage Fats Oil and Grease (see comments above)

  - Gas Stations/fueling operations will need to address fueling oil water separator and trench drain calcs.

  - Dumpster pads cannot drain directly to storm drain.

LOT RESTRICTIONS/LIMITATIONS: (must be identified on the Lot Summary Chart on the cover sheet)

- Environmental Protection Area signs, RPA, SPA, wetlands

- Building Permits delayed due to sediment basins/traps

NO COMMENTS

PLANNING COMMISSION RECOMMENDATION:

The Environmental Section:

can recommend approval of this project to the Planning Commission.

cannot recommend approval of this project to the Planning Commission because:

Reviewed by:	John Woodburn

Date Reviewed:	3 April 2014

Phone Number:	501-5851		Revised 5/9/11