LAND-DISTURBANCE TYPE DETERMINATION AND APPLICABLE REQUIREMENTS

Using the Land-Disturbance Type Determination Worksheet (attached) found in Chapter 3 of the Henrico County Environmental Compliance Manual (Manual), this project has been determined to be (one of the following):

only a Virginia Erosion and Sediment Control Program (VESCP) land-disturbing activity

only a Virginia Stormwater Management Program (VSMP) land-disturbing activity

only a Chesapeake Bay Preservation Act (CBPA) land-disturbing activity

both a VESCP land-disturbing activity and a VSMP land-disturbing activity

both a VESCP land-disturbing activity and a CBPA land-disturbing activity

none of the above – NO COMMENTS - an Environmental Compliance Plan (ECP) is not required

Based on Table 5.1 in Chapter 5 of the Environmental Compliance Manual and the land-disturbance determination made above, an ECP must be developed that contains the following components:

General information in accordance with Section 5.3 of the Manual

CBPA requirements in accordance with Chapter 6 of the Manual

An Environmental Site Assessment in accordance with Chapter 7 of the Manual

An Erosion and Sediment Control (ESC) plan in accordance with Chapter 8 of the Manual

A Stormwater Management (SWM) plan in accordance with Chapter 9 of the Manual

A Pollution Prevention Plan in accordance with Chapter 10 of the Manual

Total Maximum Daily Load (TMDL) information in accordance with Chapter 11 of the Manual

A Stormwater Pollution Prevention Plan (SWPPP) in accordance with Chapter 13 of the Manual

Municipal Separate Storm Sewer System (MS4) Program requirements in accordance with Chapter 15 of the Manual

This project has been determined to be a VSMP land-disturbing activity.  Therefore, a General Construction Permit (GCP) must be obtained prior to commencement of land-disturbance in accordance with Chapter 12 of the Manual.

ADDITIONAL COMMENTS:

GRANDFATHERED AND  PREVIOUSLY PERMITTED PROJECTS

This project is neither grandfathered nor previously permitted.

Application of the Technical Criteria found in Chapter 14 of the Manual (old Technical Criteria) is only allowed on grandfathered projects or projects that obtained initial GCP coverage prior to July 1, 2014 as described in Chapter 4 of the Manual.  However, the Technical Criteria found in Section 9.3 of the Manual (new Technical Criteria) may be applied at the applicant’s discretion in lieu of those in Chapter 14.

This project has claimed grandfathered status.

Before grandfathered status can be confirmed, information verifying compliance with the following conditions must be provided:

For local, state, and federal projects:

There has been an obligation of funding, either in whole, or in part, prior to July 1, 2012, or a stormwater management plan for the project was approved by the Department or the Administrator prior to July 1, 2012.

No General Construction Permit (GCP) was issued prior to July 1, 2014.

Land-disturbance did not commence prior to July 1, 2014.

For private projects:

A currently valid proffered or conditional zoning plan, a preliminary or final subdivision plat, a preliminary or final site plan, zoning plan with a plan of development, a comprehensive stormwater management master plan;  or any document determined to be equivalent to one of the above was approved by the Administrator by July 1, 2012.

The approved document provides for a layout.

The resulting activity will be compliant with the technical stormwater management requirements in Chapter 14 of the Manual.

No General Construction Permit (GCP) was issued prior to July 1, 2014.

Land-disturbance did not commence prior to July 1, 2014.

The project has claimed initial GCP coverage was obtained prior to July 1, 2014.

Provide evidence of the previously issued GCP, including project limits.

This status has been confirmed based on information provided verifying compliance with the applicable conditions described in Chapter 4 of the Manual.

Project status (grandfathered, previously permitted, etc.) must be identified on the cover sheet.

ADDITIONAL COMMENTS:

- A Stormwater Pollution Prevention Plan (SWPPP) is required for all proposed VSMP land-disturbing activities.

- The following information must be provided so that it can be included in the SWPPP binder that will be distributed at the pre-construction meeting:

Tab 1 - SWPPP title sheet

Tab 3 - Required SWPPP Components table

Tab 4 - SWPPP narrative

Tab 7 – ECP and Other Incorporated Plans

Tab 8 - Pollution Prevention Plan Information

Tab 9 - TMDL table 9.1

SWM facility information sheets

- All outlet protection must be designed in accordance with Std. & Spec. 3.18 of the Virginia Erosion and Sediment Control Handbook, Third Edition, 1992.

- Show the dimensions for all outlet protection (length, width, and depth, including filter fabric lining).

- Label the limits of the 100-year floodplain as “variable width drainage and utility easement” and “Special Flood Hazard Area”.

EASEMENTS / AGREEMENTS:

- Show the location, width, and recordation information for all existing drainage easements. For the pipe system Ex70-71 to the northwest.

- The Deed Book and Page Number must be provided for all proposed off-site drainage easements prior to plan approval. For the pipe system Ex70-71

- Provide documentation from all private utility companies (power, gas, etc.) that authorizes land disturbance within their easements.

TECHNICAL CRITERIA FOR GRANDFATHERED & PREVIOUSLY PERMITTED PROJECTS (Chapter 14)

- The following worksheets (if checked) must be corrected/completed and submitted to the Department of Public Works and also included in the plans.

Worksheet 14.09 – Program Implementation		Worksheet 14.01 – Situation One,

Worksheet 14.06 – Urban Management Area Opt In		Worksheet 14.02 – Situation Two,

Worksheet 14.08 – Environmental Fund Contribution		Worksheet 14.03 – Situation Three,

Worksheet 14.04 – Situation Four, or

Worksheet 14.07 – Compliance		Worksheet 14.05 – Situation Five

BMP design worksheet

Provide Water Quality Calculations for this Phase showing that the site is under 16% and No BMP’s are required.  Keep the overall Water Quality Calculations in the plan.

- To evaluate whether or not dams/impoundments are subject to the Virginia Dam Safety Act, Article 2, Chapter 6, Title 10.1 of the Code of Virginia and Dam Safety Regulations, the following information must be provided:  Applies to proposed Sediment Basin in the northeast corner of the site

dam height (vertical distance from the streambed at the downstream toe to the top of dam)

the impoundment capacity (the volume capable of being impounded at the top of the dam)

- If the dam height is greater than three (3), a geotechnical certification must be submitted in accordance with Section 3-14 of the Henrico County Design Manual stating that construction compaction requirements have been achieved.  This must be submitted as part of the BMP as-built certification prior to ESC bond release. Applies to proposed Sediment Basin in the northeast corner of the site

- Complete the “Outfall Adequacy” table on the ESC/ESA sheet. This plan is under the “old regs”; therefore use the old Outfall Adequacy Table.  You were told in error to use the new outfall tables.

- All sediment basins/traps must drain to an adequate outfall in accordance with MS-19.  Provide supporting information on the plans to show that this requirement is being met. Include the Sediment Trap #5 along the north property line against I-64

- Additional comments may follow upon review of a subsequent submittal.

ADDITIONAL COMMENTS:

  - Provide details and hydraulic calculations for the outfall channel from OF-200. From outfall to existing inlet.  Why are the pipes not being connected to the existing offsite storm sewer system?

  - Provide evidence that you can tie into the storm sewer system on the property to the west. Could not locate agreement on the plans.

  - All work in West Broad Street R/W is under VDOT purview and not part of these comments.

- Profile the outfalls down to the center of the RPA creek to show it drains.

- Show the level spreaders in the profile to show they fit into the area.

- 20-feet is the max depth for “BB” series inlets per VDOT Guidelines.  You might want to consult with a structural engineer for inlet design. Inlets 300, 452 & 460 exceed 20-ft.

- Consider including the 3 &4 BB Series inlet details on the plans.

- Page C10.03 - In the Channel Computation Table, is that supposed to be “15-yr Normal Depth” or “10-yr”?

- Page C10.04 – In the “Convergence Point Narrative”, it appears the narrative abruptly ends.  Is there something missing?

The Engineering Section has completed its review and has no comments at this time.

OTHER REVIEW AGENCIES

Please see the attached comments from the Environmental Division

Please see the attached comments from the Traffic Engineering Division

PLANNING COMMISSION RECOMMENDATION

The Engineering Section:

can recommend approval of this project to the Planning Commission

cannot recommend approval of this project to the Planning Commission because:

.

Reviewed by:	Steve Bandura

Date Reviewed:	08oct14

Phone Number:	804-501-4616

JULY 2014