Project Name: Shady Grove United Methodist Church Expansion Phase I

POD #:

Tidemark #: POD2017-00249

Planner: Christina Goggin      		Due Date:6/9/2017

STANDARD COMMENTS:

- Designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s office.   Please provide a layout for your planned fire lane designation. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices must be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

- If the type of construction, furnishings and the layout of the structure(s) prevent adequate performance of the communication system utilized by emergency services, the owners will be required to install the necessary devices to obtain communication coverage inside the structure(s). This will be determined after all furnishings and occupants are in the structure.

These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2012 Virginia Statewide Fire Prevention Code, which identifies the 2012 International Fire Code as a technical reference.

The following areas need attention:

Provide ISO calculations for all structures planned on 1980 rating schedule.

Provide hydrants to satisfy needed fire flow as established by the ISO calculations.  The following

GPM credits, as per ISO Standards will apply.  Hydrant within 300 feet of structure = 1000 GPM;

301 feet to 600 feet = 670 GPM;   over 600 feet = 250 GPM.

Hydrants must be within a 350 feet hose lay of the most remote part of the structure and a minimum of 50 feet from the structure wall and accessible to fire department apparatus.  Measure hose as laid from apparatus.

Hydrants must be between 1½ feet and 7 feet from the curb line and have 4 inch opening facing the street, unless otherwise instructed by the Fire Marshal’s office.

Project Name:

Page 2

Provide a dedicated hydrant to serve as supply for the fire department connections.  Fire department connections should be 50 feet from the structure.  The dedicated hydrant shall be no closer than 20 feet and no further than 50 feet to the fire department connection.

Relocate hydrants as shown on plans.

A 20 feet fire department access road shall extend within 150 feet of all portions of the structure.

No two hydrants shall be closer than 30 feet to each other.

No fire hose lay allowed across four lane roadway (48 feet or more).

Fire lanes may be required, minimum 20 feet in width.  If the fire lane exceeds 150 feet in length,

a cul-de-sac shall be provided, with a turning radius of 48 feet to accommodate fire apparatus,

Additional Comments:

- Please include the (Fire lane Guideline) attached, to the site Plans for Contractor’s information.

Russell Rastegar					Date:  5/22/17

Fire Protection Engineer

Assistant fire marshal

Office (804) 501-5793

Cell (804) 380-919