COMMONWEALTH OF VIRGINIA

COUNTY OF HENRICO

R. Joseph Emerson, Jr., AICP

Director of Planning

(804) 501-4602

October 16, 2017

David Maruskin, P.E.

Draper Aden Associates

8090 Villa Park Drive

Richmond, Virginia 23228			RE:	POD-094-97 Admin.

Tidemark #POD 2014-00399

Fareva -Aerosol

2300 Darbytown Road

Construction Plan Review Comments

##### Dear Mr. Maruskin:

Please be advised that the planning review of the construction plans submitted for review on September 27, 2017, has been completed.  Based upon this review, the Planning Department has the following comments, which may delay approval of your construction plan:

- Identify the limits of pavement and curb and gutter in the loading dock expansion area. And, provide applicable construction details, .including storm water facilities.

- Identify the location and provide dimensional details for the proposed pipe bridge extension in the loading dock expansion area.

- Identify the location and provide dimensional details for the proposed gas houses and vestibules in the loading dock expansion area. Including door swings.

- Identify the location and design details for the proposed stairway and gate located at the southern end of the loading dock expansion area. Provide landings on both sides of the gate

- Identify the location and provide design details for any fencing proposed in the loading dock expansion area. Chain link fencing should be black vinyl coated and grounding details provided as necessary.

- Identify the location of the telecommunications box enclosure in the loading dock expansion area.

- Indicate if there is an easement to the telecommunications box and if so if the proposed gas house encroaches into the easement,

- Given the close proximity of the existing telecommunications box to one of the proposed gas houses, indicate if special grounding and/or explosion proof design is required. Provide a letter from the utility provider (Verizon/Comcast) indicating the proposed work does not conflict with their facilities.

- Given the close proximity of an existing underground electric service to one of the proposed gas houses indicate if special grounding or explosion proof design is required.  Provide a letter from Dominion Virginia Power if applicable indicating the proposed work does not conflict with their facilities.

- Identify how the loading dock expansion area is going to be secured/ fenced to limit access by utility employees and their agents during gas house operations.

- The existing conditions and erosion and sediment control plans were not revised to reflect either existing conditions or the proposed improvements in the loading dock expansion area revise plans accordingly..

- Consider potential conflicts of underground utilities crossing under the proposed extension of the pipe bridge, in particular footings and guidewires for the pipe bridge supports.

- Provide locations and details of any warning signs in the proposed loading dock expansion area.

- Identify the location and provide details including photometrics and cut sheets for any proposed site lighting fixtures and poles in the loading dock expansion area. Indicate if special grounding or explosion proof design is required.

- Identify gasses carried in the pipe bridge and provide MSDS sheets to the Fire Marshall for review.

Please note additional comments will be provided under separate cover by the Departments of Public Work and Public Utilities. Please resubmit 9 sets of revised plans for review along with one set of annotated comments. Once all comments are addressed, you will be advised to submit plan sets for signature.

If you have any questions, or if I can be of further assistance, please call me at 501-5920

Sincerely,

Michael F. Kennedy

County Planner

pc: Fareva Richmond, Inc., Att.: David Keaney

Fareva Richmond, Inc.

Att.: David Keaney

2248 Darbytown Road

Henrico, VA 23231