The design, construction, and maintenance of stormwater management facilities are governed by the specifications included in Section 9.4 of the Henrico County Environmental Compliance Manual.  The following checklist only identifies the information and details that must be included in the SWM plan.

PLAN REQUIREMENTS:

- Provide a site map identifying pertinent information regarding the Underground Detention (ED) Pond.

The contributing drainage area (CDA) boundaries, acreage, and land cover;

Topography of the site area including the ED pond area, its CDA, and any pre-treatment practices;

The locations of all conveyance system outfalls into basin must be shown.

- Provide profiles and section views that show the following:

|  | Emergency spillway elevation |
| --- | --- |
|  | Principal spillway crest |
| 10-year storm elevation | Principal spillway and embankment |
| 50-year storm elevation | Energy balance volume detention elevation |
| 100-year storm elevation |  |

- Provide a plan view showing:

| Sizing and dimensions for all components | Emergency spillway and exit channel |  |
| --- | --- | --- |
| Delineation of the 50-year (if applicable) and 100-year storm elevation in and around the basin |  |  |

- Provide a detail of the principal outlet structure showing:

| Trash racks |
| --- |
| Orifice sizing and elevations | Dewatering device anti-clogging information | Material and sizing information for all components |
| 1-year, 10-year, 50-year, and 100-year storm elevations, where applicable |

ADDITIONAL COMMENTS:

COMPUTATIONS:

- Hydrologic analysis must be based on a 24-hour storm event using site specific rainfall precipitation frequency data recommended by the U.S. National Oceanic and Atmospheric Administration (NOAA) Atlas 14.

- The U.S. Department of Agriculture’s Natural Resources Conservation Service (NRCS) synthetic 24-hour rainfall distribution and models, including but not limited to TR-55 and TR-20; hydrologic and hydraulic methods developed by the U.S. Army Corps of Engineers;  or other standard hydrologic and hydraulic methods must be to conduct the analyses necessary to demonstrate compliance with the stormwater quality and quantity requirements of Chapter 9 of the Henrico County Environmental Compliance Manual.

- The Rational Method may only be used for evaluating peak discharges such as pipe sizing.

- The Modified Rational Method may only be used for evaluating volumetric flows to stormwater conveyances and may not be used to perform basin routings.

- Provide pre- and post-development hydrologic, hydraulic, and routing information for the 1- year, 2- year, 10- year, and 100-year, 24-hour storms, as needed, for all underground detention basins.:

- Provide pre- and post-development hydrologic, hydraulic, and routing information for the 1- year, 2- year, 10- year, 50-year, and 100-year, 24-hour storms, as needed, for 50/10 detention facilities.

- Provide the complete input used for the hydrograph generation on the plans.

- Provide a stage/storage table.

- Provide a stage/discharge for each component of the outlet structure.

- Provide a composite stage/discharge table.

- Provide an outlet control analysis.

MAINTENANCE:

- A Maintenance Agreement (for other practices) is required, identifying the person or organization responsible for maintenance and authorizing access for inspections and maintenance.

- Provide a summary of the long term maintenance requirements and the owner inspection requirements (frequency and who can perform the inspections) for the SWM facility on the SWM plan.

Reviewed by:	Conner Barnes, EIT

Date Reviewed:	1/26/2018

Phone Number:	804-501-5851

APRIL 2016