Project Name: Comfort inn &Suites @ Richmond Airport

Tidemark #: POD2019-00071		Planner: Spencer Norman

Due Date: 3/1/19

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- The dedicated hydrant is not in an acceptable location due to the interference with parking spaces and the dumpster enclosure.

- The hydrant at Sta 11+00 is too close to the building.  Relocate to a location a minimum 50’ away from the exterior wall.

- The FDC is too close to the building. Relocate to the minimum 50’ from the exterior wall.

The painted fire lane markings shown on the plan do not reflect the Henrico county fire lane standard.  Remove them from the plans and the signs that are part of the standard.

- Demonstrate maneuvering clearance for a 47’ fire apparatus on the plans.

- Confirm the cantilevered canopy at the entrance meets the minimum 14’ vertical clearance.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 2/20/19

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us