Project Name: Project Isaac

Tidemark #: POD2019-00105	 		Planner: Tony Greulich

Due Date: 4/15/19

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- The most recent submittal has not resolved the comments from the previous submittal, however, as those comments were minor in nature and the plan is schematically acceptable, Division of Fire Recommends approval to the Planning Commission.

- Will the Guard House be staffed 24/7/365?

- Will the Guard House have gates?

- Provide an elevation view detail for all gates proposed. Call out dimensions for height and clearance width.

- Confirm if each FDC will serve the entire building it connects to.  If so, 2 FDCs per building may be eliminated.  If an ISO hydrant is in the vicinity of the dedicated Hydrant, the D.H. may be eliminated as well.

- Show the Henrico County Fire Lane Guidelines on the plan.

- Provide fire lane signs around the perimeter of both building on the inside curb line.  For the road between the two buildings you may elect to mark either side (only one side is required to be marked).

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 4/3/19

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us