Project Name: Dominion Boulevard Apartments – Phase I

Tidemark #: POD2020-00117			Planner: Tony Greulich

Due Date: 3/27/20

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- The FDC and dedicated Hydrant shall be located on the same side of the drive aisle.

- The FDC shall be located with 50’ of the dedicated hydrant.

- Show the location of the FDC and dedicated hydrant for the parking garage standpipe.

- The site does not meet minimum hydrant spacing.

- Fire lane signs shall be spaced between 75-100’.

- Fire lane signs shall not be placed within any portion of a CG-12.

- Confirm the parking garage meets the open parking garage requirements of VCC (2015) section 406.5.2.

- Provide standpipe outlets for each courtyard.  It is recommended to coordinate with the architect and provide   connections from the interior standpipe system rather than a dry horizontal standpipe.

- The alignment of the doors from the lobbies to the courtyards of both buildings and the walkway for building A1 are beneficial to fire and is requested to be maintained for the use of ground ladders.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 3/19/20

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us