Project Name: Laurel Park

Tidemark #: POD2021-00049			Planner: Spencer Norman

Due Date: 2/26/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- Fire lanes signage is required to be located on both ides of drive aisle that are 20-26’ foot in width.  Please revise plans accordingly.

- Painted fire lane markings are not required.

- Additional Fire lane signs will be required throughout the project.

- The FDC and Dedicated hydrant for building 2 are blocked by parking stalls.  Please revise location of both.

- The FDC for the retail building is blocked by parking stalls and is too far from the dedicated hydrant.  Revise to show a remote FDC.

- The hydrant north west of unit 53 is too close to the dedicated hydrant.  Revise the location to be atleast 50 away along the drive aisle.  Recommend placing it closer to unit 53 near the curve for the garage entrance.

- A method to provide firefighting water to the interior of the courtyard is required.  If the building will have standpipes in the stairwells, it is recommended that additional outlets be provided at the doorways into the courtyard, rather than providing a dry horizontal standpipe.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 2/17/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us