Project Name: Highland Park

Tidemark #: POD2021-00149				Planner: Aimee Crady

Due Date: 4/23/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- Provide a proposed layout for fire lane signage.

- Additional hydrants are needed, please coordinate with the DPU reviewer.

- FDCs are required to be located on the same side of the drive aisle as their respective dedicated hydrants.

- The arrangement of 3 FDCs in front of building 8 is likely to cause confusion at an emergency scene.  As a suggested resolution to this, relocate the FDC for building 6 to the front of that building.  The new dedicated hydrant for that FDC will serve as an ISO hydrant for building 7 and 8.

- Add a note stating that signage will be provided for every FDC, indicating which buildings they will serve.

- A Separate meeting with Fire and DPU may be beneficial to resolve comments in an expeditious manner.

- Additional comments may be generated upon resubmittal.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 4/16/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us