Project Name: Virginia Center Commons Townhomes Section 1

Tidemark #: POD2021-00121			Planner: Spencer Norman

Due Date: 4/30/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- Advisory comment:  The 18’ road width is acceptable to fire per the exception to SFPC 503.2.1.  This exception requires the proposed townhomes to be sprinklered.  If the plan were to be revised to eliminate the sprinkler systems, the roads would be required to meet 20’ minimum.  Please note that road widths are also governed by the requirements of other departments.

- Provide a proposed layout for fire lane markings.  Given the nature of the project, fire lane markings shall be stenciled on the roadway.  The markings shall be in 12” yellow letters and state “NO PARKING FIRE LANE”.  The markings shall be within the first 50’ of the roadway and then spaced every 100’.  The markings shall be placed on both sides of the drive aisle and faced to be read in the direction of travel.  Signs will not be required.

- Additional fire hydrants are required.  Please coordinate with the DPU reviewer to address this comment.

- As fire department access to the proposed units is dependent upon the access drive to the west, provide an access easement to ensure this drive aisle can be maintained if that property is sold in the future.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 4/21/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us