Project Name: 3500 West View

Tidemark #: POD2021-00197			Planner: Mike Kennedy

Due Date: 5/28/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- The FDC location is not acceptable.  The FDC shall be placed in a location where it cannot be readily blocked by vehicles.

- A method of providing fire-fighting water to the interior of the courtyards is required.  This can be accomplished either by providing a standpipe connection from the interior standpipe system to the doors to the courtyards or by providing a Dry Horizontal Standpipe.

- The utility Plans appears to be mislabeled as sheet C-201 “Grading and Drainage Plan”

- Provide a proposed layout for fire lane signage.

- Will the parking garage have standpipes or sprinklers?  How will they be supplied?

- There is currently a route through units 155 and 156, and units 169 and the pass through that will allow a ground ladder to be placed in the pool courtyard and allow for a ladder rescue from an interior balcony.  Consider providing a similar route for the amenity courtyard.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 5/17/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us