Project Name: The Corner at Twin Hickory Condominiums

Tidemark #: POD2021-00194			Planner: Spencer Norman

Due Date: 6/4/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- Provide a leader line call out for the FDCs or provide the symbol in the legend.

- For the comments listed below indicated with an asterisk, please coordinate with this reviewer and Mrs. Togba-Lee with Henrico Building Inspections.

- *The Private fire line shall be looped and provide sectional valves per NFPA 24 (2013) Section 6.6.1.  This is required when the number of connections to the system exceed 6.

- *Per VCC 903.4, the control valves for the condo buildings are required to be monitored.  This will likely require post indicator valves to be used.

- *The fire line for building 6 appears to connect to the public water line and not the private fire loop.

- Provide a proposed layout for fire lane signage.

- The Construction type on the ISO Calculations does not match the construction type on the cover sheet.

- Until the comment below is addressed, Fire cannot recommend planning commission approval.

- Provide a turning radius demonstration using the 47’ fire apparatus.  Show this for all turns throughout the project, but primarily for the turnaround in front of buildings 6 and 7.

- Additional comments may be generated upon response to these comments.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 5/24/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us