The design, construction, and maintenance of stormwater management facilities are governed by the specifications included in Section 9.4 of the Henrico County Environmental Compliance Manual.  The following checklist only identifies the information and details that must be included in the SWM plan.

VA DEQ DESIGN SPEC NO. 2:  SHEET FLOW TO A VEGETATED FILTER STRIP OR CONSERVED OPEN SPACE

Although two design variants are specified in the VA BMP Clearinghouse (filter strip or conserved open space), use of this practice in Henrico County must incorporate conserved open space (to eliminate flooding or other drainage related problems on adjacent property).

Use of this practice must be in accordance with Henrico County Minimum Design Standard 14.01 – Energy Dissipator

MINIMUM DESIGN CRITERIA:

- The Conserved Open Space must meet the following minimum design criteria.  The items checked below have not been properly addressed:

The groundcover must be undisturbed soils with native vegetation.

The overall slope and width must conform to the following:

The slope for the first 10 feet of filter cannot exceed 2%, and

If the slope is 0.5% - 3%, the width must be at least 35 feet; or

If the slope is 3% - 6%, the width must be at least 50 feet.

The conserved open space must be located outside of the site’s limits of disturbance and protected by ESC controls.

The conserved open space must extend downstream and tie directly into a RPA/SPA buffer, mapped special flood hazard area, or other protected area.

- The level spreading device must be designed as  Design A / Design B in accordance with Henrico County Design Standard 14.01 – Energy Dissipator.

- The sides and bottom of the plunge pool excavation shall be lined with filter fabric underlining and Class AI rip rap in accordance with the Virginia Erosion and Sediment Control Handbook, Third Edition, 1992, State Minimum Standards and Specifications Number 3.19.

- The spreader weir section must be constructed by excavating a trench to the depth and configuration shown, laying down hardware cloth and backfilling with VDOT No. 3 aggregate.  The hardware cloth shall be galvanized steel, ½ inch mesh, 19 gauge and shall be wrapped around the aggregate and timber as shown.  The edges must be stapled to the top of the timber every 12” with ¾ inch galvanized steel staples.

- The 6” x 6” treated timber must be level.

- Special considerations must be made where a cross slope exists in the area of construction and outfall, and where there is a possibility that storm water may flow around and bypass the spreader weir.  An additional timber and aggregate weir section is required that ties back into existing grade.

- A minimum of clearing and grading may be required downstream of the spreader weir section to insure free overflow of storm water over the weir.  Generally, all clearing and grading shall be kept to a minimum, but where required, the disturbed area shall be planted with sod in accordance with the Virginia Erosion and Sediment Control Handbook, Third Edition, 1992, State Minimum Standards and Specifications Number 3.33.  The sod shall be secured with netting and staples in accordance with Plate 3.33-2.

- If installed at the end of county maintained storm sewer, the drainage easement must continue through the level spreading device.  This easement does not encompass the entire spreader device.

ADDITIONAL COMMENTS

- Please show in plan view the distance between the level spreader and the stream channel.

PLAN REQUIREMENTS:

8.	 	Provide a site map identifying the following pertinent information regarding Sheet Flow to Conserved Open Space:

The contributing drainage area (CDA) boundaries, acreage, and land cover;

Topography of the site including the SWM facility, its CDA, and any pre-treatment practices;

A soil map for the site and area of the facility.

The areas of the site compensated for in the water quality calculations.

9.		Provide profiles and section views that show the following:

| inflow pipe/channel inverts |  |
| --- | --- |
| Side slopes |  |
| Weir elevation |  |
| Elevation of dissipator storage section bottom |  |
| Dissipator section inverts |  |
| Elevation of conserved open space below weir (must be at least two inches below the inflow pipe/channel invert |  |

- Provide a plan view showing:

| Dimensions - length and width of dissipator section and dissipator storage section |  |  |
| --- | --- | --- |
| Length of weir |  |  |
| Flow length through Conserved Open Space |  |  |
| Drainage easement through SWM facility |  |  |

- The plans must clearly indicate that the SWM facility has been designed in accordance with Section 9.4.2 (Sheet Flow to Conserved Open Space) of the Henrico County Environmental Compliance Manual.

ADDITIONAL COMMENTS

- In the storm profile on sheet C13, please call out (and label) the elevations of the features of the level spreader (dissipator storage section, weir, etc). Please also provide spot shots of existing ground just below the weir as well as at approximately 10, 20, and 30 feet downstream of the level spreader

- For the level spreader detail on sheet C19, please show the spot elevations that were used to determine the slopes downstream of the level spreader. (0.8%, 0.6%, and 1.5%)

- For the level spreader detail on sheet C19, please label the features of the level spreader that the elevations are provide for (dissipator storage section, etc)

COMPUTATIONS:

- Hydrologic analysis must be based on a 24-hour storm event using site specific rainfall precipitation frequency data recommended by the U.S. National Oceanic and Atmospheric Administration (NOAA) Atlas 14.

- Provide the post-development hydrologic for the 10-year peak discharge for all discharge points entering the facility.

ADDITIONAL COMMENTS

- Please delineate on sheet C15 (VRRM Drainage Area Map) the area that drains to the level spreader.

- How was the flow of 0.07 cfs for the 1” storm determined on sheet C19? This value seems low.

MAINTENANCE:

- A Maintenance Agreement (for other practices) is required, identifying the person or organization responsible for maintenance and authorizing access for inspections and maintenance.

- Provide a summary of the long term maintenance requirements and the owner inspection requirements (frequency and who can perform the inspections) for the SWM facility on the SWM plan.

ADDITIONAL COMMENTS

ACCESS:

- All SWM facilities shall be designed to provide the following for adequate access for maintenance activities:

An access area at least 20 feet in width must be provided to the SWM facility from a public road

An access area 20 feet in width must be provided around the SWM facility that encompasses the highest continuous contour within the SWM facility.

The access areas must either be in common area or located completely on an individual lot

The access areas cannot contain any obstacles, or vegetation that would prevent access of maintenance equipment;

The access areas shall not exceed a grade or cross-slope of 12:1.

The access area to the SWM facility must be constructed of load bearing materials

The access area must provide sufficient turn-around area;

- The access areas identified above must be in an easement that provides access to the County for SWM facilities located in single-family residential developments.

ADDITIONAL COMMENTS

LOCATION:

- SWM facilities cannot be located within the public right-of-way limits.

- The SWM facility must be located to the rear of all buildable areas or in common area that is controlled and maintained by a Homeowners Association.

ADDITIONAL COMMENTS

CONSTRUCTION:

- The sequence of construction must address the SWM facility installation and appropriate inspections, including:  initial site preparation, excavation/grading, and installation of the weir.  We recommend that County staff be involved in these inspections.

- The sequence of construction must clearly state that a construction record drawing and certification that the stormwater management facility has been constructed in accordance with the approved plan must be submitted to the County and approved prior to Environmental Compliance Bond (ECB) release.

ADDITIONAL COMMENTS:

- Please include items 20 and 21 in the E&S Phase 2 Narrative

Reviewed by:	Alex Gruendl

Date Reviewed:	30 July 2021

Phone Number:	804-501-4033

July 2014