Project Name: One Pouncey

Tidemark #: POD2021-00318				Planner: Mike Kennedy

Due Date: 9/17/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2015 Virginia Statewide Fire Prevention Code, which identifies the 2015 International Fire Code as a technical reference.

- Show the dedicated hydrant and FDC connection for all buildings that will be sprinklered.

- A method or providing firefighting supplies to the interior of the courtyard is required.  Consider providing a connection from the in-building standpipe system adjacent to the doors to the courtyard.

- The hydrant immediately north of budling 3 is too close to the building.

- Painted curbs are not required for fire lane markings.

- Fire lane signs are required to be placed on both sides of the drive aisle where the drive aisle width is less than 26 feet.

- A significant number of additional fire lane signs are required.  Contact the reviewer to discuss.

- Provide ISO Needed Fire Flow Calculations.

- Additional hydrants may be required after ISO calculations have been provided.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 9/9/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us