Project Name: 2001 Dabney Road

Tidemark #: POD2021-00486			Planner: Mike Kennedy

Due Date: 12/6/21

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Advisory comment: Comments on this plan are cursory in nature due to the level of detail proved on the conceptual plan.  Please refer to Division of Fire’s POD Review guidelines prior to submitting full plans.

- The bend in the road in the northeast corner does not appear to meet the required minimum turning radius.  This shall be demonstrated on the full plan set using the 47’ apparatus turn template

- The drive aisle on the north and east sides on the building exceed the maximum distance without an approved turnaround.  See VSFPC appendix D for approved turnaround design and dimensions.

- Based on the height and size of the building, the east drive aisle will need to be increased to 24’.

- There appears to be inadequate locations for the placement of fire hydrants while maintaining minimum separation distance.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 11/19/21

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us