Project Name: Old Three Chopt Apartments

Tidemark #: POD2022-00011				Planner: Mike Kennedy

Due Date: 1/28/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Show how fire-fighting supplies water are provided to the interior courtyards.  The preferred method is by providing outlets connected to the buildings standpipe system to the doors exiting to the courtyard.

- Will the building pre protected with a NFPA 13 or 13R sprinkler system?  A full 13 system will suffice for the needed hose lay increase for the portion of the building the fronts Gayton Road.

- Consult Division of Fires POD Review guidelines.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 1/19/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us