Project Name: I-895 Logistics Center

Tidemark #: POD2022-00048				Planner: Tony Greulich

Due Date: 2/25/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Provide a detail for the bollards protecting the private fire hydrants.  The bollards shall conform to SFPC (2018) section 312.

- Provide details for the gate that separates the site from the emergency access.  The detail shall include that a Knox padlock will be provided.  Chain and Bollard is not an acceptable gate.

- Complete the use group and construction type fields on the cover sheet.

- Provide a proposed layout for fire lane signage.  Where drive aisles are 20-26’ signs are required on both sides of the drive aisle; where the drive aisle is 26-32’, provide signs on one side only.  Where greater than 32’ signs are not required.

- Show the Henrico County Fire Lane Guidelines on the plan.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 2/10/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us