Project Name: Coca-Cola Bottling Co – Warehouse Building Expansion

Tidemark #: POD2022-00098			Planner: Tony Greulich

Due Date: 3/25/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Provide details for the gate across the 24’ drive aisle. A knox padlock shall be provided.

- Provide the “click 2 enter” system at the gate at the guard shack.

- Provide a proposed layout for fire lane signage.

- Show “No Parking Fire Lane” painted markings in front of the fire hydrant in the northwest corner of the proposed building.

- Define the 12’x12’ markings north of the proposed building.

- Provide a copy of the most recent fire pump flow test performed on the existing fire pump, showing that it can meet the design discharge.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 3/16/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us