Project Name: HCA at Gateway Square

Tidemark #: POD2022-00329			Planner: Aimee Crady

Due Date: 7/1/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Fire cannot support Director’s Agenda approval due to the comments listed below.

- The drive aisle to east of the building exceeds the maximum distance for a fire lane without a turn around.

- The Dedicated Hydrant and FDC are located behind parking stalls.

- Revise the location of the FDC so that it is located on the same side of the drive aisle as the dedicated hydrant.

- Site does not meet the required 350’ Hose lay.

- Site does not meet the minimum number of hydrants based on the ISO Calculations.

- The Construction type on the coversheet is blank.  Revise to reflect construction types as defined by Chapter 6 in the Virginia Construction Code.

- Commercial is not a valid use group, revise to reflect the use groups as defined in chapter 3 of the Virginia Construction Code.

- The fire lane signage layout requires revision.  Please contact the reviewer directly to coordinate new locations.

- Additional comments may be generated upon resubmittal.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 6/17/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us