Project Name: Insurance Auto Auctions – Portugee Road

Tidemark #: POD2022-00305			Planner: Tony Greulich

Due Date: 7/1/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Complete the Construction type field on the cover sheet.

- Most of the Gate and Fence Details on sheet C308 are unreadable.

- Sheet C308 general note 3 indicates that the gates may be manual or electrically operated.  This need to be determined prior to approval of Construction plans.  If manually operated gates are to be used, Provide Knox pad locks for each gate.  If electronic gates are to be used, provide the “Click-2-Enter” system.

- Additional hydrants are required to meet the required 350’ hose lay.  The 350’ hose lay cannot pass through the fence without using the gates.

- Complete the ISO Needed Fire Flow calculations and show them on the plan.  Additional hydrants are anticipated to be needed to meet the required flow.

- Due to Comments 4 and 5 above, Fire cannot support Director’s agenda/Planning Commission Approval.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 6/17/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us