Project Name: Brook Road Knights Inn Apartments

Tidemark #: POD2022-00424			Planner: Christina Goggin

Due Date: 9/2/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Provide building labels or a building numbering system on the plan.

- The southernmost building and the eastern most building do not meet the hose lay required by SFPC 503.1.1. (200 feet for sprinklered buildings).

- Extend the 24’ drive aisle on the northern side of the eastern building into the green space in order to increase accessibility of Aerial Fire apparatus.  If desired, parking spaces may be placed along this drive aisle.

- Extend the sidewalk along the east side of the southern most building to facilitate the placement of ground ladders.

- Provide a proposed layout for fire lane signage.

- Revise the construction types on the cover sheet to match the construction types of the Virginia Construction Code.

- The Zoning drawing and elevations call the construction type as VA, the ISO Calculations show C-3 non-combustible.  Please clarify and revise as needed.

- The following hydrants are blocked by parking: H-8, H-18, H-20, and H-21.

- Hydrant H-14 is located such that it is not accessible to fire apparatus.  Relocate it so that it is not located at the end of a drive aisle.  For reference, H-16 is acceptable.

- Several FDCs are blocked by parking.  Remote FDCs will be required to correct this.

- Additional comments may be generated upon resubmittal.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 8/17/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us