Project Name: Gateway at Landmark Section 1

Tidemark #: POD2022-00438				Planner: Christina Goggin

Due Date: 9/9/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- The FDC is inaccessible to fire apparatus.  Relocate to an area where is it accessible from a road or drive aisle. Note: coordinate location so that is remains accessible throughout the project.

- No dedicated hydrant has been provided.

- The site does not meet the minimum number of hydrants, nor the 350’ hose lay.

- Sectional valves are required for the Private fire protection line and are to be provided in locations such that not more than 6 buildings are on a single section.

- Provide a proposed layout for fire lane signage.

- The ISO Calculations show the construction as Non-Combustible, however the cover sheet shows the construction type as “frame”. Revise the construction type on the cover sheet to match the construction types in the Virginia Construction code and revise the ISO calculations to match.

- Advisory comment:  This development relies upon the Landmark Development (Formerly Dry Bridge Commons) to obtain a second point of access as Old Memorial Drive is currently a dead end road.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 8/19/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us