Project Name: Warehouse at Lot J

Tidemark #: POD2022-00476			Planner: Spencer Norman

Due Date: 9/30/22

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Provide a proposed layout for fire lane signage.  Signs are required to be spaced every 100 feet and within 50 feet of the start of the fire lane.  Signs shall be planed on both sided of the drive aisle where less than 26 feet, and on one side of the drive aisle where width is 26-32 feet.  signs shall be angled into the direction of traffic.

- Reside the FDC from “Dedicated FDC Hydrant” to state “FDC Siamese”.

- Provide a dedicated hydrant for each FDC located off the county public waterline. The dedicated hydrant shall be located on the same side of the drive aisle as the FDC and within 50 feet.  Label the dedicated hydrant as “Dedicated Fire Hydrant”

- An additional fire hydrant is needed on the north side of the building to meet hose lay.

- An addition hydrant is needed on the southwest corner of the building to meet hose lay.

- An addition hydrant is needed on the southeast corner of the building to meet hose lay.

- Provide bollards for all private fire hydrants.

- Provide a bollard detail.  Detail shall comply with IFC 312.

- Provide ISO Needed Fire Flow Calculations on the plan.

- It is suggested to connect the north drive aisle to the western cul-de-sac in order to provide better fire access around the building.  Access may be gated if desired.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based of field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in the decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 9/19/22

Fire Plans Reviewer

Office (804) 501-5793

smi188@henrico.us