Project Name: Helios

Tidemark #: POD2023-00206				Planner: Christina Goggin

Due Date: 6/9/23

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Revise block 13D of the cover sheet to reflect construction types listed in chapter 6 of the Virginia Construction Code.

- Provide a proposed layout for fire lane signage.  Signs shall be spaced every 100 feet and within 50 feet of the start and end of the fire lane.  Signs shall be placed on both sides of the road where the road is less than 26 feet wide.

- Show the Henrico County Fire Lane Guidelines on the plan.

- The dedicated hydrant for the FDC for building one is not acceptable.  Dedicated hydrants shall be within 50 feet of the FDC and located on the same side of the drive aisle as the FDC. One possible solution to this comment is to provide a remote FDC for buildings 1 that is collocated in the island with the dedicated hydrant.

- Relocate the hydrant north of building 1 to be located along the same drive aisle as the face of the building.

- Site does not meet the minimum number or spacing of fire hydrants based on the ISO calculations.   Contact the DPU reviewer to resolve this comment.

- Provide details for the security gates: will the gates be electronically operated or  manual?  IF electronically operated, provide the “click-2-enter” system.  If manual, provide a knox padlock. Provide an elevation view of each gate.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based on field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 5/30/23

Fire Plans Reviewer

Cell (804) 380-9193

smi188@henrico.us