Project Name: Helios

Tidemark #: POD2023-00206				Planner: Christina Goggin

Due Date: 8/7/23

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Previous comment is repeated: Revise block 13D of the cover sheet to reflect construction types listed in chapter 6 of the Virginia Construction Code.

- Provide a proposed layout for fire lane signage.  Signs shall be spaced every 100 feet and within 50 feet of the start and end of the fire lane.  Signs shall be placed on both sides of the road where the road is less than 26 feet wide.

- Show the gate operators on the plan.  Indicate the operators will have the “click-2-enter” system.

- Show where the gate keypads will be located.

- Add a note to the security gate on the plan that a knox padlock will be provided.

- The provided architectural plans indicate the construction type for the clubhouse will be VB and non-sprinklered, however the ISO calculations indicate Joisted Masonry which is akin to type IIIB and a sprinkler reduction is taken.  Please correct this discrepancy and revise as needed.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based on field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 7/27/23

Fire Plans Reviewer

Cell (804) 380-9193

smi188@henrico.us