Project Name: Richmond Ford West

Tidemark #: POD2023-00351					Planner: Salim Chishti

Due Date: 9/8/23

The following comments reflect areas of the plan that do not meet the standards of Henrico Division of Fire and need attention. These comments are meant to be specific highlights to applicable codes. The expectation is placed on the developers and contractors to follow all codes including, but not limited to, the 2018 Virginia Statewide Fire Prevention Code, which identifies the 2018 International Fire Code as a technical reference.

- Additional Fire hydrants are required to meet the required hose lay.  Please consult the DPU reviewer to resolve this comment.

- Show the ISO Calculations on the plan.

- The cover sheet indicates the building is to be sprinklered.  Show the FDC and Dedicated Hydrant along with the run in to the sprinkler riser.  If these appliances are existing as part of the existing building, show their existing locations on the plan.

- Provide a propose lay out for fire lane signage. Signs are required on both side of the 24-foot drive aisle west of the proposed addition. This will require building mounted signs.

- Show the Henrico County Fire Lane Guidelines on the plan.

- Correct block 12F on the cover sheet to reflect the correct use group for vehicle repair.

The comments in the section below are standard comments and advisory in nature.  No action is required to resolve these comments:

- Fire lane markings as shown on the plan may not be adequate based on field conditions.  Final designation and marking of fire lanes will be determined prior to certificate of occupancy by the Fire Marshal’s Office. Yellow paint on pavement and curb may be required in addition to signs.

- The Division of Fire recommends the installation of “lock boxes” in all commercial construction.

- Speed bumps will increase the response time of emergency vehicles, resulting in decreased protection of life and property.  All traffic calming devices shall be approved by the Fire Marshal.

- All roadway gates must be approved by the Fire Marshal’s office.  A separate plan showing details of required features must be submitted for approval. Failure to obtain approval may result in the gates being locked in an open position until approved.  Henrico County uses the “Click-2-Enter” gate access system.

Greg Smith							Date: 8/23/23

Fire Plans Reviewer

Cell (804) 380-9193

smi188@henrico.us