COMMONWEALTH OF VIRGINIA

COUNTY OF HENRICO

R. J. Emerson, Jr., AICP

Director of Planning

(804) 501-4602

October 11, 2023

Cecil MacNair, PE

Rachet Designs

7119 Stafford Park Drive

Mosley, VA 23120

##### Re: 	POD2023-00440

##### Willow Lawn Waterline Extension (Augusta Avenue)

##### Utility Plan Review 1

##### Mr. MacNair:

Planning review of the above-referenced Utility Plan submitted for review on September 26, 2023, has been completed.  The Planning Department provides the following comments:

Identify the location of the City of Richmond/Henrico County boundary line.

Identify the location and details of the existing City of Richmond Department of Public Utilities (City DPU) water main located in Augusta Avenue.

Identify the size and location of existing City DPU water meter(s). Indicate if City DPU meters will be abandoned, or if they will be retained for domestic or irrigation use. Provide details for abandonment of existing water services as applicable. Where public water service is provided by County DPU, and sanitary sewer service is provided by City DPU; revised utility easement agreements may be required for coordination of quantity of discharge fees.

Indicate if the property being served on Augusta Avenue is in a City DPU-Water Pressure Zone. Indicate if the conversion of service from City DPU to Henrico County DPU impacts the proposed development of dwelling units on the adjoining Willow Lawn Shopping Center property.

Indicate if a cross-connection between City and County watermains is proposed and provide any necessary details.

Identify the location of any existing or proposed utility easements required for the proposed waterline extension. Provide recording information for any offsite easements for the waterline extension on the construction plans.

Provide GIS coordinates on applicable plan sheets.

Modifications to utility services provided by City DPU are subject to their review and approval.

If you have any questions, please contact me at 501-5920.

Sincerely,

Michael F. Kennedy

County Planner

P.C.: 	Jeremy Connell – jc@paretollc.com

Marchelle Sossong, PE, Henrico DPU